## 40 CFR 63 ZZZZ
Subpart ZZZZ—National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines
Applicability: | Existing stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions that commenced construction or reconstruction before December 19, 2002.
Existing stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions that commenced construction or reconstruction before June 12, 2006.
Existing stationary RICE located at an area source of HAP emissions that commenced construction or reconstruction before June 12, 2006.
New stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions that commenced construction on or after December 19,2002.
New stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions that commenced construction on or after June 12, 2006.
New stationary RICE located at an area source of HAP emissions that commenced construction on or after June 12, 2006.
Reconstructed stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions that commenced reconstruction on or after December 19, 2002.
Reconstructed stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions that commenced reconstruction on or after June 12, 2006.
Reconstructed stationary RICE located at an area source of HAP emissions that commenced reconstruction on or after June 12, 2006.
| New or reconstructed stationary RICE located at an area source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subparts IIII (for CI engines) or | [5 empty] | JJJJ (for SI engines) as applicable.
New or reconstructed 2SLB stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subpart JJJJ.
New or reconstructed 4SLB stationary RICE with a site rating ≤ 250 BHP located at a major source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subpart JJJJ.
New or reconstructed 4SRB stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subpart JJJJ.
| New or reconstructed stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions which combusts landfill or digester gas equivalent to 10% or more of the gross heat input on an annual basis must comply with this Subpart by meeting the requirements of 40 CFR 60 Subparts IIII (for CI engines) or | [5 empty] | JJJJ (for SI engines) as applicable.
| New or reconstructed emergency or limited use stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subparts IIII (for CI engines) or | [5 empty] | JJJJ (for SI engines) as applicable.
New or reconstructed CI stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions must comply with this Subpart by meeting the requirements of 40 CFR 60 Subpart IIII.
Owners or operators of an existing non-emergency, non-black start, CI stationary RICE with a site rating > 300 BHP with a displacement < 30 L per cylinder that uses diesel fuel, must use diesel fuel that meets the requirements in 40 CFR 80.510(b) for non-
Exemptions: | A new or reconstructed emergency or limited use stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions does not have to meet the requirements of 40 CFR 63 Subparts A or ZZZZ, except for the notification requirements of § 63.6645(f).
A new or reconstructed emergency or limited use stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions which combusts landfill or digester gas equivalent to 10% or more of the gross heat input on an annual basis must meet the notification requirements of § 63.6645(f) and the requirements of §§ 63.6625(c), 63.6650(g), and 63.6655(c). These stationary RICE do not have to meet the emissions limitations and operating limitations of this Subpart.
Existing SI 2SLB stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions.
Existing SI 4SLB stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions.
Existing emergency or limited use stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions.
Existing stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions that combusts landfill gas or digester gas equivalent to 10% or more of the gross heat input on an annual basis.
Existing residential, commercial, or institutional emergency stationary RICE located at an area source of HAP emissions.
Existing non-emergency CI stationary RICE loacted in Guam, American Samoa, the Commonwealth of the Northern Mariana Islands, or at area sources in areas of Alaska not accessible by the FAHS are exempt from the fuel requirements of 40 CFR 80.510(b).
General Standards: | Compliance with the numerical emission limitations established in this Subpart is based on the results of testing the average of three 1-hour runs using the testing requirements and procedures in § 63.6620 and Table 4 of this Subpart. | Existing, new or reconstructed SI 4SRB stationary RICE with a site rating > 500 BHP located at a major source of HAP emissions | you must comply with the emission limitations in | Table 1a | and the operating limitations in | Table 1b | which apply to you.
|  | New or reconstructed 2SLB, 4SLB, or CI stationary RICE with a site rating > 500 HP located at a major source of HAP emissions |  | Table 2a |  | Table 2b
|  | Existing non-emergency stationary CI RICE with a site rating > 500 BHP located at a major source of HAP emissions |  | Table 2c |  | Table 2b
|  | New or reconstructed 4SLB stationary RICE with a site rating (R) of 500 BHP > R ≥ 250 BHP located at a major source of HAP emissions manufactured on or after January 1, 2008 |  | Table 2a |  | Table 2b
|  | Existing stationary RICE with a site rating ≤ 500 BHP located at a major source of HAP emissions |  | Table 2c |  | N/A
|  | Existing stationary RICE located at an area source of HAP emissions |  | Table 2d |  | Table 1b or
Table 2b

## Table 1a
For each . . . | You must meet the following emission limitation, except during periods of startup . . . | During periods of startup you must . . .
1. 4SRB stationary RICE | a. Reduce formaldehyde emissions by 76 percent or more. If you commenced construction or reconstruction between December 19, 2002 and June 15, 2004, you may reduce formaldehyde emissions by 75 percent or more until June 15, 2007 or | Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply. 1
b. Limit the concentration of formaldehyde in the stationary RICE exhaust to 350 ppbvd or less at 15 percent O2
1 Sources can petition the Administrator pursuant to the requirements of 40 CFR 63.6(g) for alternative work practices.

## Table 1b
For each . . . | You must meet the following operating limitation . . .
1. 4SRB stationary RICE complying with the requirement to reduce formaldehyde emissions by 76 percent or more (or by 75 percent or more, if applicable) and using NSCR; or | a. Maintain your catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water at 100 percent load plus or minus 10 percent from the pressure drop across the catalyst measured during the initial performance test; and
4SRB stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust to 350 ppbvd or less at 15 percent O2 and using NSCR; or
4SRB stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust to 2.7 ppmvd or less at 15 percent O2 and using NSCR. | b. Maintain the temperature of your stationary RICE exhaust so that the catalyst inlet temperature is greater than or equal to 750 °F and less than or equal to 1250 °F.
2. 4SRB stationary RICE complying with the requirement to reduce formaldehyde emissions by 76 percent or more (or by 75 percent or more, if applicable) and not using NSCR; or | Comply with any operating limitations approved by the Administrator.
4SRB stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust to 350 ppbvd or less at 15 percent O2 and not using NSCR; or
4SRB stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust to 2.7 ppmvd or less at 15 percent O2 and not using NSCR.

## Table 2a
For each . . . | You must meet the following emission limitation, except during periods of startup . . . | During periods of startup you must . . .
1. 2SLB stationary RICE | a. Reduce CO emissions by 58 percent or more; or | Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply. 1
b. Limit concentration of formaldehyde in the stationary RICE exhaust to 12 ppmvd or less at 15 percent O2. If you commenced construction or reconstruction between December 19, 2002 and June 15, 2004, you may limit concentration of formaldehyde to 17 ppmvd or less at 15 percent O2 until June 15, 2007
2. 4SLB stationary RICE | a. Reduce CO emissions by 93 percent or more; or
b. Limit concentration of formaldehyde in the stationary RICE exhaust to 14 ppmvd or less at 15 percent O2
3. CI stationary RICE | a. Reduce CO emissions by 70 percent or more; or
b. Limit concentration of formaldehyde in the stationary RICE exhaust to 580 ppbvd or less at 15 percent O2
1 Sources can petition the Administrator pursuant to the requirements of 40 CFR 63.6(g) for alternative work practices.

## Table 2b
For each . . . | You must meet the following operating limitation . . .
1. 2SLB and 4SLB stationary RICE and CI stationary RICE complying with the requirement to reduce CO emissions and using an oxidation catalyst; or 2SLB and 4SLB stationary RICE and CI stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust and using an oxidation catalyst; or 4SLB stationary RICE and CI stationary RICE complying with the requirement to limit the concentration of CO in the stationary RICE exhaust and using an oxidation catalyst | a. maintain your catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water at 100 percent load plus or minus 10 percent from the pressure drop across the catalyst that was measured during the initial performance test; and
b. maintain the temperature of your stationary RICE exhaust so that the catalyst inlet temperature is greater than or equal to 450 °F and less than or equal to 1350 °F. 1
2. 2SLB and 4SLB stationary RICE and CI stationary RICE complying with the requirement to reduce CO emissions and not using an oxidation catalyst; or 2SLB and 4SLB stationary RICE and CI stationary RICE complying with the requirement to limit the concentration of formaldehyde in the stationary RICE exhaust and not using an oxidation catalyst; or 4SLB stationary RICE and CI stationary RICE complying with the requirement to limit the concentration of CO in the stationary RICE exhaust and not using an oxidation catalyst | Comply with any operating limitations approved by the Administrator.
1 Sources can petition the Administrator pursuant to the requirements of 40 CFR 63.8(g) for a different temperature range.

## Table 2c
For each . . . | You must meet the following requirement, except during periods of startup . . . | During periods of startup you must . . .
1. Emergency stationary CI RICE and black start stationary CI RICE. 1 | a. Change oil and filter every 500 hours of operation or annually, whichever comes first; 2 | Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply. 3
b. Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. 3
2. Non-Emergency, non-black start stationary CI RICE < 100 HP | a. Change oil and filter every 1,000 hours of operation or annually, whichever comes first; 2
b. Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. 3
3. Non-Emergency, non-black start CI stationary RICE 100 ≤ HP ≤ 300 HP | Limit concentration of CO in the stationary RICE exhaust to 230 ppmvd or less at 15 percent O2
4. Non-Emergency, non-black start CI stationary RICE 300 < HP ≤ 500 | a. Limit concentration of CO in the stationary RICE exhaust to 49 ppmvd or less at 15 percent O2; or
b. Reduce CO emissions by 70 percent or more.
5. Non-Emergency, non-black start stationary CI RICE >500 HP | a. Limit concentration of CO in the stationary RICE exhaust to 23 ppmvd or less at 15 percent O2; or
b. Reduce CO emissions by 70 percent or more.
6. Emergency stationary SI RICE and black start stationary SI RICE. 1 | a. Change oil and filter every 500 hours of operation or annually, whichever comes first; 2
b. Inspect spark plugs every 1,000 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. 3
7. Non-Emergency, non-black start stationary SI RICE < 100 HP that are not 2SLB stationary RICE | a. Change oil and filter every 1,440 hours of operation or annually, whichever comes first; 2
b. Inspect spark plugs every 1,440 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 1,440 hours of operation or annually, whichever comes first, and replace as necessary. 3
8. Non-Emergency, non-black start 2SLB stationary SI RICE < 100 HP | a. Change oil and filter every 4,320 hours of operation or annually, whichever comes first; 2
b. Inspect spark plugs every 4,320 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 4,320 hours of operation or annually, whichever comes first, and replace as necessary. 3
9. Non-emergency, non-black start 2SLB stationary RICE 100 ≤ HP ≤ 500 | Limit concentration of CO in the stationary RICE exhaust to 225 ppmvd or less at 15 percent O2
10. Non-emergency, non-black start 4SLB stationary RICE 100 ≤ HP ≤ 500 | Limit concentration of CO in the stationary RICE exhaust to 47 ppmvd or less at 15 percent O2
11. Non-emergency, non-black start 4SRB stationary RICE 100 ≤ HP ≤ 500 | Limit concentration of formaldehyde in the stationary RICE exhaust to 10.3 ppmvd or less at 15 percent O2
12. Non-emergency, non-black start landfill or digester gas-fired stationary RICE 100 ≤ HP ≤ 500 | Limit concentration of CO in the stationary RICE exhaust to 177 ppmvd or less at 15 percent O2
1 If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the work practice requirements on the schedule required in Table 2c of this subpart, or if performing the work practice on the required schedule would otherwise pose an unacceptable risk under Federal, State, or local law, the work practice can be delayed until the emergency is over or the unacceptable risk under Federal, State, or local law has abated. The work practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under Federal, State, or local law has abated. Sources must report any failure to perform the work practice on the schedule required and the Federal, State or local law under which the risk was deemed unacceptable.
2 Sources have the option to utilize an oil analysis program as described in § 63.6625(i) in order to extend the specified oil change requirement in Table 2c of this subpart.
3 Sources can petition the Administrator pursuant to the requirements of 40 CFR 63.6(g) for alternative work practices.

## Table 2d
For each . . . | You must meet the following requirement, except during periods of startup . . . | During periods of startup you must . . .
1. Non-Emergency, non-black start CI stationary RICE ≤ 300 HP | a. Change oil and filter every 1,000 hours of operation or annually, whichever comes first; 1 | Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply.
b. Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first;
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.
2. Non-Emergency, non-black start CI stationary RICE 300 <HP≤ 500 | a. Limit concentration of CO in the stationary RICE exhaust to 49 ppmvd at 15 percent O2;or
b. Reduce CO emissions by 70 percent or more.
3. Non-Emergency, non-black start CI stationary RICE > 500 HP | a. Limit concentration of CO in the stationary RICE exhaust to 23 ppmvd at 15 percent O2; or
b. Reduce CO emissions by 70 percent or more.
4. Emergency stationary CI RICE and black start stationary CI RICE. 2 | a. Change oil and filter every 500 hours of operation or annually, whichever comes first; 1
b. Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.
5. Emergency stationary SI RICE; black start stationary SI RICE; non-emergency, non-black start 4SLB stationary RICE > 500 HP that operate 24 hours or less per calendar year; non-emergency, non-black start 4SRB stationary RICE > 500 HP that operate 24 hours or less per calendar year. 2 | a. Change oil and filter every 500 hours of operation or annually, whichever comes first; 1
b. Inspect spark plugs every 1,000 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.
6. Non-emergency, non-black start 2SLB stationary RICE | a. Change oil and filter every 4,320 hours of operation or annually, whichever comes first; 1
b. Inspect spark plugs every 4,320 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 4,320 hours of operation or annually, whichever comes first, and replace as necessary.
7. Non-emergency, non-black start 4SLB stationary RICE ≤ 500 HP | a. Change oil and filter every 1,440 hours of operation or annually, whichever comes first; 1
b. Inspect spark plugs every 1,440 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 1,440 hours of operation or annually, whichever comes first, and replace as necessary.
8. Non-emergency, non-black start 4SLB stationary RICE > 500 HP | a. Limit concentration of CO in the stationary RICE exhaust to 47 ppmvd at 15 percent O2; or
b. Reduce CO emissions by 93 percent or more.
9. Non-emergency, non-black start 4SRB stationary RICE ≤ 500 HP | a. Change oil and filter every 1,440 hours of operation or annually, whichever comes first; 1
b. Inspect spark plugs every 1,440 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 1,440 hours of operation or annually, whichever comes first, and replace as necessary.
10. Non-emergency, non-black start 4SRB stationary RICE > 500 HP | a. Limit concentration of formaldehyde in the stationary RICE exhaust to 2.7 ppmvd at 15 percent O2; or
b. Reduce formaldehyde emissions by 76 percent or more.
11. Non-emergency, non-black start landfill or digester gas-fired stationary RICE | a. Change oil and filter every 1,440 hours of operation or annually, whichever comes first; 1
b. Inspect spark plugs every 1,440 hours of operation or annually, whichever comes first; and
c. Inspect all hoses and belts every 1,440 hours of operation or annually, whichever comes first, and replace as necessary.
1 Sources have the option to utilize an oil analysis program as described in § 63.6625(i) in order to extend the specified oil change requirement in Table 2d of this subpart.
2 If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the management practice requirements on the schedule required in Table 2d of this subpart, or if performing the management practice on the required schedule would otherwise pose an unacceptable risk under Federal, State, or local law, the management practice can be delayed until the emergency is over or the unacceptable risk under Federal, State, or local law has abated. The management practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under Federal, State, or local law has abated. Sources must report any failure to perform the management practice on the schedule required and the Federal, State or local law under which the risk was deemed unacceptable.

## Table 4
For each . . . | Complying with the requirement to . . . | You must . . . | Using . . . | According to the following requirements . . .
1. 2SLB, 4SLB, and CI stationary RICE | a. Reduce CO emissions | i. Measure the O2 at the inlet and outlet of the control device; and | (1) Portable CO and O2 analyzer | (a) Using ASTM D6522-00 (2005) a (incorporated by reference, see § 63.14). Measurements to determine O2 must be made at the same time as the measurements for CO concentration.
|  | ii. Measure the CO at the inlet and the outlet of the control device | (1) Portable CO and O2 analyzer | (a) Using ASTM D6522-00 (2005) a, b (incorporated by reference, see § 63.14) or Method 10 of 40 CFR appendix A. The CO concentration must be at 15 percent O2, dry basis.
2. 4SRB stationary RICE | a. Reduce formaldehyde emissions | i. Select the sampling port location and the number of traverse points; and | (1) Method 1 or 1A of 40 CFR part 60, appendix A § 63.7(d)(1)(i) | (a) Sampling sites must be located at the inlet and outlet of the control device.
|  | ii. Measure O2 at the inlet and outlet of the control device; and | (1) Method 3 or 3A or 3B of 40 CFR part 60, appendix A, or ASTM Method D6522-00m (2005) | (a) Measurements to determine O2 concentration must be made at the same time as the measurements for formaldehyde concentration.
|  | iii. Measure moisture content at the inlet and outlet of the control device; and | (1) Method 4 of 40 CFR part 60, appendix A, or Test Method 320 of 40 CFR part 63, appendix A, or ASTM D 6348-03 | (a) Measurements to determine moisture content must be made at the same time and location as the measurements for formaldehyde concentration.
|  | iv. Measure formaldehyde at the inlet and the outlet of the control device | (1) Method 320 or 323 of 40 CFR part 63, appendix A; or ASTM D6348-03 c, provided in ASTM D6348-03 Annex A5 (Analyte Spiking Technique), the percent R must be greater than or equal to 70 and less than or equal to 130 | (a) Formaldehyde concentration must be at 15 percent O2, dry basis. Results of this test consist of the average of the three 1-hour or longer runs.
3. Stationary RICE | a. Limit the concentration of formaldehyde or CO in the stationary RICE exhaust | i. Select the sampling port location and the number of traverse points; and | (1) Method 1 or 1A of 40 CFR part 60, appendix A § 63.7(d)(1)(i) | (a) If using a control device, the sampling site must be located at the outlet of the control device.
|  | ii. Determine the O2 concentration of the stationary RICE exhaust at the sampling port location; and | (1) Method 3 or 3A or 3B of 40 CFR part 60, appendix A, or ASTM Method D6522-00 (2005) | (a) Measurements to determine O2 concentration must be made at the same time and location as the measurements for formaldehyde concentration.
|  | iii. Measure moisture content of the stationary RICE exhaust at the sampling port location; and | (1) Method 4 of 40 CFR part 60, appendix A, or Test Method 320 of 40 CFR part 63, appendix A, or ASTM D 6348-03 | (a) Measurements to determine moisture content must be made at the same time and location as the measurements for formaldehyde concentration.
|  | iv. Measure formaldehyde at the exhaust of the stationary RICE; or | (1) Method 320 or 323 of 40 CFR part 63, appendix A; or ASTM D6348-03 c, provided in ASTM D6348-03 Annex A5 (Analyte Spiking Technique), the percent R must be greater than or equal to 70 and less than or equal to 130 | (a) Formaldehyde concentration must be at 15 percent O2, dry basis. Results of this test consist of the average of the three 1-hour or longer runs.
|  | v. Measure CO at the exhaust of the stationary RICE | (1) Method 10 of 40 CFR part 60, appendix A, ASTM Method D6522-00 (2005) a, Method 320 of 40 CFR part 63, appendix A, or ASTM D6348-03 | (a) CO Concentration must be at 15 percent O2, dry basis. Results of this test consist of the average of the three 1-hour longer runs.
a You may also use Methods 3A and 10 as options to ASTM-D6522-00 (2005). You may obtain a copy of ASTM-D6522-00 (2005) from at least one of the following addresses: American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohocken, PA 19428-2959, or University Microfilms International, 300 North Zeeb Road, Ann Arbor, MI 48106. ASTM-D6522-00 (2005) may be used to test both CI and SI stationary RICE.
b You may also use Method 320 of 40 CFR part 63, appendix A, or ASTM D6348-03.
c You may obtain a copy of ASTM-D6348-03 from at least one of the following addresses: American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohocken, PA 19428-2959, or University Microfilms International, 300 North Zeeb Road, Ann Arbor, MI 48106.