## Slide 1: Module 21: Chemical Addition
Drinking Water Plant Operator Certification Training

## Slide 2: Chemical Addition Topics
Unit 1 – Chemicals Used in Water Treatment
Unit 2 – Safety and Handling
Unit 3 – Chemical Dosage Calculations
Unit 4 – Chemical Feed Systems

## Slide 3: Unit 1 – Chemicals Used in Water Treatment
Learning Objective
  When given a source water problem, participants will be able to identify on the Chemical Usage Table those chemicals used to address and correct the problem in the treatment of drinking water.

## Slide 4: Chemical Uses
Coagulation Chemicals
pH Adjustment
Taste and odor control
Trace elements and Heavy Metals
Corrosion Control and Sequestering
Fluoridation
Disinfection

## Slide 5: Coagulating Chemicals
The addition of coagulant chemicals promotes the destabilization of the smaller, non-settleable particles and colloidal particles resulting in the aggregation of these particles into larger, more settleable floc.
Types of coagulating chemicals?
Ferric Chloride
Aluminum Chloride

## Slide 6: Types of Coagulant Chemicals
Coagulants
Primary Coagulants
Coagulant Aids

## Slide 7: Common primary coagulant chemicals and their corresponding pHs
Common Primary Coagulant Chemicals |  | 
Type | Chemical | pH
Aluminum Salts | Dry Alum (Aluminum Sulfate) | 3.3-3.6
 | Liquid Alum (Aluminum Sulfate) | 2.1
 | Poly Aluminum Chloride | 1.8
Iron Salts | Ferric Chloride | less than 2
 | Ferric Sulfate | 1

## Slide 8: pH

## Slide 9
If you add |  | The pH will be:
Potassium hydroxide | KOH | Raised
Nitric Acid | HNO3 | Lowered
Calcium Hydroxide Hydrated Lime | Ca(OH)2 | Raised
Calcium Hydroxide Slaked Lime | Ca(OH)3 | Raised
Sulfuric Acid | H2SO4 | Lowered
Sodium Hydroxide AKA: Caustic Soda | NaOH | Raised
Soda Ash | Na2CO3 | Raised
Hydrochloric Acid | HCl | Lowered

## Slide 10: Practically every phase of water treatment is pH dependent.
pH
Iron and
Manganese
Removal
Coagulation
Efficiency
Corrosion
Control
Treatment
Disinfection
By-product
Creation
Disinfection Efficiency

## Slide 11: Alkalinity
Alkalinity is a measure of the capacity of water or any solution to neutralize or “buffer” acids. This measure of acid-neutralizing capacity is important in figuring out how “buffered” the water is against sudden changes in pH. Alkalinity should not be confused with pH.

## Slide 12: Chemical Impacts on Alkalinity
1 part alum uses 0.5 parts alkalinity for proper coagulation
1 part ferric chloride will consume 0.92 parts alkalinity for proper coagulation
Sodium bicarbonate (Bicarbonate Soda) will make water more alkaline. It can be used when you only want to increase the alkalinity.
pH adjustment chemicals may also increase alkalinity. Therefore, alkalinity may be increase by the addition of lime, caustic soda or soda ash.

## Slide 13: Taste and Odor
Taste and odor in drinking water are among the most common and difficult problems that confront waterworks operators.
Various chemicals are added to remove tastes and odors. There are two general methods for controlling tastes and odors.
Removal of the causes of the tastes and odors
Destruction of taste and odor causing compounds

## Slide 14: Removal of Trace Elements and Heavy Metals
In small quantities, certain heavy metals are nutritionally essential for a healthy life, but large amounts of any of them may cause acute or chronic toxicity (poisoning).
There are three processes by which these removals are accomplished:
Oxidation
Improved Coagulation/Flocculation/Sedimentation
Lime Softening

## Slide 15: Corrosion Control and Sequestration
Corrosive water is characterized by pH and alkalinity values that are somewhat lower than they should be for the water to be considered “stable”.
Chemical Treatment of Corrosive Water:
  Stabilizing the water.
  The use of corrosion inhibitors.

## Slide 16: Fluoridation
Fluoride is added to the drinking water to improve the development of teeth and bones in young children!
Most commonly added fluoridation chemicals:
  sodium fluoride
  sodium silicofluoride
  hydrofluosilicic acid
Please note: any fluoride chemical is nasty. Please wear the appropriate PPE like a face shield, rubber apron, and rubber gloves!

## Slide 17: Disinfection
Disinfection kills or inactivates disease-causing organisms in a water supply.
There are two kinds of disinfection:
Primary disinfection achieves the desired level of microorganism kill or inactivation.
Secondary disinfection maintains a disinfectant residual in the finished water that prevents the regrowth of microorganisms.

## Slide 18: Chemical Usage Table
Key Information on various chemicals for your reference

## Slide 19: Unit 1 Exercise
Coagulation
Coagulant aids
pH
Alkalinity
Calcium and Magnesium
Sequestering agents
Primary disinfection
Secondary disinfection

## Slide 20: Question 9
If you add: | The pH will be raised or lowered
NaOH | Raised
Aluminum Sulfate | Lowered
Ca (OH)2 | Raised
Sulfuric Acid | Lowered
H2SiF6 | Lowered
Ferric Chloride | Lowered
Na2CO3 | Raised

## Slide 21: Unit Quiz Questions 10/11
1. List the chemicals you might add to control odor. Include the chemical name and best feeding form for each.
Activated Carbon - Dry to form slurry
Ozone – Gas
Pot Permanganate - Dry to form solution
Sodium Chlorite - Dry or solution
Chlorine – Gas
Sodium Hypochlorite – Solution
2. Name several chemicals which might be added during the coagulation process.
Aluminum Sulfate - Coagulant
Ferric Chloride - Coagulant
Ferric Sulfate - Coagulant
Poly Aluminum Chloride -Coagulant
Calcium Hydroxide-pH Adjustment
Calcium Oxide - pH Adjustment
Sodium Bicarbonate - pH Adjustment
Sodium Carbonate - pH Adjustment
Sodium Hydroxide - pH Adjustment
Polymers - Coagulant Aid

## Slide 22: Unit 2 Key Points
  Page 1-16 in the workbook

## Slide 23: Unit 2 – Safety and Handling
Learning Objectives
  When given a Material Safety Data Sheet and specific chemical names, identify specific information related to chemical characteristics and other information provided .
  List the five components of Chemical Handling Equipment.

## Slide 24: Parts of the SDS
16 required sections
Now available electronically (pull it up on your phone!)

## Slide 25: Five Components of Chemical Handling Equipment
  Selection of Equipment – follow the SDS
  Labels and Warning Signs
  Breathing Protection
  Protective Clothing
  Protective Equipment.

## Slide 26: Emergency Response Planning
An emergency response plan (ERP) must be developed to help a system protect public health, limit damage to the system and the surrounding area, and help a system return to normal as soon as possible. Employees who are prepared know what actions must be taken in the event of an emergency.
A good ERP includes:
Contact information
Assessment of Available Resources
Corrective Actions For Probable Emergency Situations

## Slide 27: Unit 2 Key Points
The single most important resource for finding information about a chemical is the Material Safety Data Sheet (MSDS).
When using chemicals, protections are necessary. These protections include labels, signs, and safe chemical handling equipment. Not all chemicals require the same protections.
A good Emergency Response Plan contains contact information, an assessment of available resources to be used in the event of an emergency in addition to corrective actions which describe the types of emergency measures to be taken.

## Slide 28: Unit 3 – Chemical Dosage Calculations
Learning Objective
  When given the formula and required data, calculate chemical dosages for each of the following: Dry Chemicals, Liquid Chemicals, and Gaseous Chemicals .

## Slide 29: Feed Systems
Feed system need to deliver chemicals into the treatment system at rates necessary for optimal performance. When designing a chemical feed system consider:
Building redundancy into the system so if there is a failure or malfunction in the primary system, a secondary system can be used.
Checking the feed pump dosage range. Feed pumps should be sized so that chemical dosages can be changed to meet varying conditions.
Evaluating the condition of the chemical feed system regularly. Preventative maintenance is critical for avoiding process upsets due to equipment breakdown.
Ensuring a good stock of repair parts for all critical equipment.

## Slide 30
Flow
Cylinder
Chemical Storage
Suction Assembly
  Foot Valve
  Suction Strainer
Calibration Chamber
Four-Function Valve
  Anti-Siphon Valve
  Back Pressure Relief Valve
  Pressure Relief Valve
  Priming Function
Pulsation Dampener
Injector Assembly
Liquid Feed Pump
Chemical Feed System

## Slide 31: Mechanical Diaphragm Metering Pump
Pump pulling chemical from the storage container:
Valve Closed
Discharge Check Valve
(Outlet)
Suction Check Valve
(Inlet)
Valve Open
Diaphragm
Plunger moves left

## Slide 32: Mechanical Diaphragm Metering Pump
Chemical is pushed in to the system.
Valve Open
Valve Closed
Suction Check Valve
(Inlet)
Discharge Check Valve
(Outlet)
Plunger moves right
Diaphragm

## Slide 33: Adjusting Chemical Feed Pump Dosage
The output of the pump is controlled by the length of the plunger stroke and the number of repetitions of the stroke (the speed and the stroke). Pumps may be controlled manually or by a rate of flow meter (flow pacing).

## Slide 34: Liquid Chemical Feed System Operation and Maintenance
Observe all operating components daily.
Maintain a regular schedule of maintenance on all equipment as per the manufacturer’s recommendations
Chemical metering pumps should be calibrated on a regular basis or when the operator suspects a problem with the pump (pump calibration demonstration to follow).
Any leak throughout the system will cause a reduction in the amount of chemical solution pumped. All leaks must be repaired as soon as they are discovered.
  If the pump looks to be operating, but the chemical feed is less than expected, suspect a ruptured diaphragm.
The suction assembly on a chemical metering pump should be inspected and cleaned on a regular basis as per the manufacturer’s recommendations.
All components that contact the chemical solution that is pumped should be disassembled, cleaned and inspected as per the manufacturer’s recommendations.

## Slide 35: Dry Chemical Feed Systems
Used to feed chemicals like:
  Lime
  Fluoride
  Carbon
  Potassium permanganate
  A dry feeder measures dry chemical and mixes it with water in a solution tank. The resulting solution is either pumped into the main water flow of the system or fed in using an ejector. An ejector system uses the Venturi effect to create a vacuum and moves the solution into the main water flow.

## Slide 36: Volumetric Dry Feeders
Chemical is usually stored in a silo above the unit and each time the system needs to make a new batch of solution a feed mechanism (rolls or screws) to deliver exactly the same volume of dry chemical to the dissolving tank with each complete revolution.

## Slide 37: Gravimetric Dry Feeders
This is a belt-type feeder that delivers a certain weight of material with each revolution of the conveyor belt.

## Slide 38: Dry Chemical Feed System Operation and Maintenance
Observe operating components daily.
Follow manufacturer’s recommendations when performing maintenance.
These units are feeding fine powdery chemicals therefore cleaning and inspection of all moving parts should be conducted routinely.
After all preventative maintenance has been completed, proper calibration should be completed.

## Slide 39: Detention Time
Detention time indicates the amount of time a give flow of water is retained by a unit process. It is calculated as the tank volume divided by the flow rate:
Detention Time Equation
Theoretical Detention Time (minutes) = Volume of Tank (gallons) Influent Flow (gpm)
Volume units match = gallons
Time units match = minutes

## Slide 40: There are two basic ways to consider detention time:
Detention time is the length of time required for a given flow rate to pass through a tank.
Detention time may also be considered as the length of time required to fill a tank at a given flow rate.
Flow
Flow
Flow

## Slide 41: Example 3.1 – Detention Time Calculation
A sedimentation tank holds 50,000 gallons and the flow into the plant is 500 gpm. What is the detention time in minutes?
Detention Time (time) = Volume = 50,000 gallons
Flow 500 gpm
= 100 minutes

## Slide 42: Example 3.2 – Detention Time Calculation
A tank is 20 feet by 35 feet by 10 feet. It receives a flow of 650 gpm. What is the detention time in minutes?
1. First must find volume (in gallons) then plug into Detention Time formula.
Volume = L x W x H 20 feet x 35 feet x 10 feet = 7,000 ft3
2. Convert to gallons from ft3
gallons = 7,000 ft3 x 7.48 gallons = 52,360 gallons
ft3
3. Plug into: Detention Time (time) = Volume =
Flow
52360 gallons = 81 minutes
650 gpm

## Slide 43: Example 3.3 – Detention Time Calculation
A flash mix chamber has a volume of 450 gallons. The plant flow is set at 5 MGD. What is the detention time of the flash chamber is seconds? (Assume the flow is steady and continuous).
First, convert the flow rate from MGD to gps (5 MGD = 5,000,000 gpd)
  5,000,000 gal x day x min = 58 gallon
day 1440 min 60 seconds second
Plug into: Detention Time (time) = Volume =
Flow
450 gallons = 8 seconds
58 gps

## Slide 44: Example 3.4 – Detention Time Calculation
A water treatment plant treats a flow of 1.5 MGD. It has 2 sedimentation basins, each 20 feet wide by 60 feet long, with an effective water depth of 12 feet. Calculate the Theoretical Sedimentation Detention Time with both basins in service (in hours).
Volume of something rectangular:
V = L x W x D
60 ft x 20 ft x 12 ft = 14,400 ft3
You have two tanks to take into account
14,400 ft3
x 2
28,800 ft3
You have to convert to gallons =
28,800 ft3 x 7.48 = 215,424 gallons
Convert from MGD to gpd = 1.5 x 1,000,000 = 1,500,000 gpd
D.T = Volume of Tank = 215,424 gallons = 0.14 days
Flow 1,500,000 gpd
Hours = .14 days x 24 hours = 3.4 hours
day

## Slide 45: Precipitation:
The chemical conversion of soluble substances (including metals) into insoluble particles.

## Slide 46: Purpose of Coagulation
Coagulating chemicals are added to water causing particles to become chemically destabilized and clump together to form floc.
• Coagulation is the destabilization of colloidal particles brought about by the addition of a chemical reagent known as a coagulant.
The amount or dosage of a precipitant, coagulant, or flocculant needed to precipitate and remove substances in water solutions is dependent on many factors.

## Slide 47
How do we know if our coagulant dosage is correct?
Jar Testing is a laboratory procedure that simulates coagulation, flocculation, and precipitation results with differing chemical dosages.

## Slide 48: Jar Tests Evaluation
Evaluate test results in each container:
Visual evaluation or measure turbidity with turbidimeter.
Rate of floc formation
Type of floc
Floc settling rate
Clarity of settled water

## Slide 49: Dry Chemical Solution Day Tanks
A day tank is used to store a limited supply of diluted chemical solution to be fed into the treatment system. The solution in a day tank can be diluted to a specific concentration (strength). The solution consists of two parts:
Solute: The dry product that you are adding or the amount of dry product in a concentrated solution.
Solvent: The liquid which is dissolving the solute.
Solute
Solvent

## Slide 50: Example 3.5 – Example Dry Feed Solution Tank Mixing
How many pounds of dry chemical must be added to a 50 gallons day tank to produce a 0.5% solution?
Hint: Every gallon of water weighs 8.34 pounds.
Pounds = 8.34 pounds x 50 gallons x 0.005 =
gallon
2.1 pounds

## Slide 51: Example 3.6 – Example Dry Feed Solution Tank Mixing
How many pounds of dry chemical must be added to a 35 gallon tank to produce a 2% solution?
Pounds = 8.34 pounds x 35 gallons x 0.02 =
gallon
5.8 pounds

## Slide 52: Jar testing is used to determine a chemical dosage!
Once the chemical dosage has been determined, the feed rate can be calculated.
“The Pounds Formula”
Chemical Feed Rate in Pounds = Plant Flow in MGD x Dosage mg x 8.34
Day L
Davidson Pie Chart
Feed Rate
Lbs
Day
MGD
Dose
Mg
L
8.34

## Slide 53: Example 3.7 – Example Dry Feed Rate Calculation
How many pounds of lime are needed for a desired dosage of 17 mg/L when the average daily plant flow is 200 GPM?
Feed Rate
? Lbs
Day
? MGD
Dose
17 mg L
8.34
200 GPM – must convert to MGD
200 x 1440 = ?
1,000,000
Chemical Feed Rate in Pounds = Plant Flow in MGD x Dosage mg x 8.34
Day L
=.288 MGD x 17 mg x 8.34 = 40.8 lb
L day
What would the feeder output be in lb/hour?
Lb = 40.8 lb x 1 Day = 1.6 lbs
Hr Day 24 Hour hr

## Slide 54: Active Strength is the percentage of a chemical or substance in a mixture that can be used in a chemical reaction.
Active strength of liquid chemicals must be known.
  Different strength chemicals can be purchased.
Active strength differs with different chemicals.
  50% Sodium Hydroxide will weigh approximately 6.38 lb/gallon.
  Aluminum Sulfate (Liquid Alum) @ 5.48 lb active/gallon
Active strength of same chemical may differ with different shipments.
  Actual strength should be tested periodically.
  Measure specific gravity and compare with known values.
  Specific gravity is the weight of a particle, substance, or chemical solution in relation to the weight of an equal volume of water (the weight of water is 8.34 pounds/gallon).

## Slide 55: Example 3.8 – Specific Gravity Calculation
The measured specific gravity of the 11% strength Ferric Chloride delivered to your plant is 1.38. Find how much each gallon weighs.
Pounds of ferric chloride = 1.38 x 8.34 = 11.5 pounds/gal
(in one gallon)

## Slide 56: Example 3.9 – Specific Gravity Calculation
How much does a 55 gallon drum of zinc orthophosphate weigh if the MSDS says the specific gravity of zinc orthophosphate is 1.46?
Pounds of Zinc Orthophosphate = 1.46 x 8.34 = 12.2 lbs/gal
(in on gallon)
So for 55 gallons, 12.2 x 55 = 671 pounds

## Slide 57: Example 3.10 – Liquid Feed Rate Calculation
A treatment plant is feeding caustic soda at a dosage of 32 mg/L. The plant flow is 347 GPM. The caustic soda is a 50% solution and has a density of 12.8 lbs/gal. What is the feed rate in pounds/day? How many gal/day of caustic would the system use?
Feed Rate
? Lbs
Day
Dose
32 mg L
8.34
GPM – must convert to MGD
347 x 1440 = ?
1,000,000
? MGD
Solve for 100% strength:
Chemical Feed Rate in Pounds = Plant Flow in MGD x Dosage mg x 8.34
Day L
= 0.5 MGD x 32 mg x 8.34 = 133 lb @ 100% Strength
L day
Convert to 50% strength:
50% = 133 lbs = 266 lbs At 50% Strength
.50 day
Compute the feed rate in gal/day: (use the density - 12.8 lbs/gal)
Gal = 266 lbs x gal = 20.8 gal
Day day 12.8 lbs day

## Slide 58: Example 3.11 – Liquid Chemical Feed Calculation
A water treatment plant uses liquid alum for coagulation. At a plant flow rate of 2.0 MGD, an alum dosage of 12.5 mg/l is required. The alum has an active chemical strength of 5.48 lb/gallon. Compute the required alum feed rate in gallons/day.
Feed Rate
? Lbs
Day
MGD
Dose
8.34
Chemical Feed Rate in Pounds = Plant Flow in MGD x Dosage mg x 8.34
Day L
= 2 MGD x 12.5 mg x 8.34 = 208.5 lb
L Day
Compute the feed rate in gal/day: (active chemical strength is 5.48 lb/gal).
Gal = 208.5 lbs x gal = 38 gal
Day day 5.48 lbs day

## Slide 59: Theoretical Pump Output
Pump Output =
Maximum Pump Output x % Speed x % Stroke
For example, if a 24 GPD pump is set at 80% stroke length and 100% speed, the theoretical pump output would be:
Pump output = 24.0 gal x 1.0 x 0.80 = 19.2 gal
day day

## Slide 60: Example 3.12 – Theoretical Pump Output
An operator wants to estimate the approximate speed and stroke settings on a diaphragm pump that is rated to deliver a maximum pump output of 24 gallons per day. The system needs to deliver approximately 15 gallons per day of sodium hypochlorite. Where would the speed and stroke need to be set?
This is a guessing game of sorts; however, go again with the concept of a higher speed setting and a stroke setting between 20% and 80%.
Pump Output = Maximum Pump Output x % Speed x % Stroke
= 24 gal x 0.90 x 0.70
day
= 15 gal
Day
So the speed could be set at 90% and the stroke could be set at 70%

## Slide 61: Liquid Feeder Operation Test Results – Alum Feed Pump Output
Pump Setting (% Full Speed) | Alum Pumped (ml) | Time (sec)
0 | 0 | 30
20 | 62.6 | 55
40 | 121.1 | 59
60 | 196.8 | 61
80 | 130.7 | 32
100 | 162.9 | 35

## Slide 62: Liquid Feeder Operation Test Results Figure 3.3
Pump Setting (%) | Alum Pumped (ml) | Time (sec) | Feed Rate (ml/min) | Feed Rate (gal/min)
0 | 0.0 | 30 | 0.00 | 0.000
20 | 65.6 | 55 | 71.56 | 0.019
40 | 141.9 | 59 | 144.31 | 0.038
60 | 249.1 | 61 | 245.02 | 0.065
80 | 195.2 | 32 | 366.00 | 0.097
100 | 267.4 | 35 | 458.40 | 0.121

## Slide 63: Example 3.14 – Liquid Feed Calculations
Using Figure 3.3, if the plant ran for 8 hours, determine how many ml the pump would deliver at a pump setting of 20%. How many gallons would you expect to use?
Total Volume (ml) = 71.56 ml x 8 hrs x 60 min = 34,348.8 ml
min 1 hour
Total Volume (gal) = 34,348.8 ml x gal = 9 gallons
3785 ml

## Slide 64: Alum Pump Calibration Curve
Please note: the two axes on a calibration curve graph are the feed rate and pump setting.

## Slide 65: Gas Feeders
Types of Gas Feeders
Direct feed
  Gas is fed directly under pressure to flow stream to be treated
Solution feed
  Gas is drawn by vacuum through piping system
  Requires use of ejector to create necessary vacuum for operation
  Ejector – a device used to disperse a chemical solution into water being treated. Find more info with chlorinators.

## Slide 66: Key Points
Once it is determined what chemical is needed for treatment, it must be determined how much chemical must be applied.
A calibration cylinder is used to determine a pumps feed rate.
The amount of chemical applied to a treatment system over a given period of time is called the feed rate.
The most common types of positive displacement pumps are peristaltic and diaphragm.
In order to calculate feed rate, unit conversions may be necessary. Unit conversion is the process of standardizing values in a calculation.
Whether the chemical is a solid, liquid, or gas a feed rate can be determined.
The output of a chemical feed pump is controlled by the length of the plunger stroke and the number of repetitions of the stroke (speed and stroke).
An ejector system uses the Venturi effect to create a vacuum and move solution into the main water flow.
A volumetric dry feeder uses a rotating feed screw to deliver a consistent volume of dry chemical into a dissolving tank; varying the speed of the rotating feed screw changes the feed rate.
A gravimetric dry feeder uses a belt to deliver a certain weight of material with each revolution of a conveyor belt.
A pump calibration curve graph shows chemical Feed Rates Vs Pump Settings.
It is important to consult with your engineer, manager, or chemical vendor to determine the active strength of the chemical. This information may also be on the MSDS.
Suction assembly consist of a suction strainer (used to protect the internal parts of a pump) and a foot valve (used to prevent the pump from loosing prime).

## Slide 67: Unit 4 – Chemical Feed Systems
Learning Objectives
  Identify storage considerations for dry, liquid and gaseous chemicals.
  When given a Typical Feed Schematic for any of the four systems, identify which system is being illustrated through the schematic.

## Slide 68: Adequate Supply
Provide sufficient chemicals in storage to insure an adequate supply at all times.
General Guideline – Provide a minimum chemical storage of the larger of:
      30 day’s supply at average usage, or
      10 day’s supply at maximum usage

## Slide 69: Storage Facilities
Dependant on quantity of chemical to be stored.
Bulk storage tanks for large amounts:
Minimum 110% of maximum delivery quantity
Drum Storage for smaller amounts.
All liquid storage and feed equipment should be stored in chemically resistant containment areas.
Areas should be large enough to contain a spill of 110% of the largest single container.
Containment areas should contain leak detection equipment to provide an alarm in the event of a chemical spill.

## Slide 70: Typical Bulk Dry Chemical Feed System

## Slide 71: Typical Bag Dry Chemical Feed System

## Slide 72: Typical Batch Dry Chemical Feed System

## Slide 73: Typical Bulk Liquid Chemical Feed System

## Slide 74: Typical Drum Storage Liquid Feed System

## Slide 75: Polymer
Polymer is shipped either dry (bags) or liquid (drums), Therefore storage facilities need to be the same as other chemicals of similar type.
Polymer must be activated prior to feeding to obtain expected results.

## Slide 76: Typical Dry Polymer Feed System

## Slide 77: Typical Liquid Polymer Feed System

## Slide 78: Gaseous Chemical Feed
  Need a separate storage and feed room
  Feed Equipment Includes:
    Vacuum Regulator – controls vacuum operated systems.
    Automatic Switchover System – provides for continuous gas supply. Automatically switches to a standby container in the event the active container becomes empty.
    Gas Feeder – controls gas feed rate.
    Ejector – produces the vacuum under which vacuum type systems operate.

## Slide 79: Accessory Equipment for Gaseous Chlorine Feed System
Evaporator – used at large installations to convert gas from liquid phase to gaseous phase, permitting higher withdrawal rate from the ton container.
Gas Solution Distributors – provides method where a single properly sized ejector can be used to split gas solution to several different feed points.
Container Scales – used to measure the quantity of gas remaining in the containers.
Gas Detectors – used to actuate an alarm if unacceptable levels of the gas are sensed in the ambient air of storage and feed rooms.
Self Contained Breathing Equipment – used to protect operation personnel in case of gas leaks or during emergency access to areas with gas leaks.
Feed Water Booster Pump – raises pressure of ejector water supply for proper operation of ejector.
Emergency Repair Kits – used to stop leaks in gas containers (2 sizes available – ton container and cylinder).

## Slide 80: Typical Gas Chemical Feed System Ton Containers

## Slide 81: Typical Small Gas Chemical Feed System

## Slide 82: Quiz – Type of Feeder System?

## Slide 83: Review Questions
Optional practice multiple choice questions.

## Slide 84: 1. ________________ _____________ add density to slow settling flocs and toughness to floc so they will not break up during the mixing and settling process.
  Primary coagulants
  Coagulant aids
  Potassium permanganate
  Zinc orthophosphate

## Slide 85: 2. A pump is rated at a maximum output of 24 gallons per day. The system feeds about 6 gallons of sodium hypochlorite each of the 2 shifts it runs. What speed and stroke setting would be expected?
  Speed of 40% and Stroke of 40%
  Speed of 50% and Stroke of 50%
  Speed of 70% and Stroke of 70%
  Speed of 80% and Stroke of 80%

## Slide 86: 3. Which of the following is (are) displacement pump(s):
  Diaphragm
  Centrifugal
  Peristaltic
  Both A and C

## Slide 87: 4. 60% hydrofluosilicic acid has a specific gravity of 1.46. How much (in pounds) does a 50 gallon drum weigh (in pounds)?
  609 pounds
  366 pounds
  44 pounds
  12 pounds

## Slide 88: 5. pH is the measure of the ______________ ____________ strength.
  hydrogen ion
  anion ion
  hydroxyl ion
  cation ion

## Slide 89: 6. Name a device which creates vacuum to move chemical solution into the main flow of water.
  Diffuser
  Ejector
  Effluent Nozzle
  Pressure Regulating Valve

## Slide 90: 7. To analyze the feed setting and feed rate, a________ _________ is needed.
  Calibration Curve
  Flow Rate
  Vacuum Regulator
  None of the above

## Slide 91: 8. The most important compounds in water which determine alkalinity:
  Calcium and Magnesium
  Carbonate and Bicarbonate
  Hydrogen and Hydroxide
  Hydrogen and Carbonate

## Slide 92: 9. Which of the following chemicals would decrease the pH of source water?
  Alum
  Ferric
  PAC
  All of the above

## Slide 93: 10. Varying the speed of rotation of the rotating feed screw varies the feed rate for which type of feeder?
  Diaphragm Feed System
  Gravimetric Feed System
  Volumetric Feed System
  None of the above

## Slide 94: 11. An emergency response plan must be developed to:
  Protect Public Health
  Limit Damage to Surrounding Area
  Help System Return to Normal Operations
  All of the above

## Slide 95: 12. ___________ is the capacity of a water to neutralize acids. This capacity is caused by the water’s content of bicarbonate, carbonate and hydroxide.
  Hardness
  pH
  Corrosivity
  Alkalinity

## Slide 96: 13. How many pounds of dry chemical must be added to a 50 gallon tank to produce a 6% solution?
  3
  25
  300
  417

## Slide 97: 14. Which chemical will increase both pH and alkalinity?
  NaHCO3
  NaOH
  KMnO4
  All of the above

## Slide 98: 15. Which of the following uses volumetric measurements to accurately deliver liquid chemicals:
  Gravimetric Feeder
  Chemical Feed Pump
  Belt Feeder
  Vibrating Feeder

## Slide 99: 16. Which chemical can be used to destroy taste and odor compounds?
  Lime
  Sulfuric Acid
  Potassium Permanganate
  None of the above

## Slide 100: 17. A water treatment plant treats a flow of 350,000 gpd. It has 2 sedimentation basins, each 10 feet wide by 30 feet long, with an effective water depth of 12 feet. Calculate the Theoretical Sedimentation Detention Time with both basins in service (in hours).
  0.15 Hours
  1.7 Hours
  0.35 Hours
  3.7 Hours

## Slide 101: 18. The clumping together of very fine particles into larger particles caused by the use of chemicals:
  Coagulation
  Flocculation
  Sedimentation
  Filtration

## Slide 102: 19. Removal of the causes of the tastes and odors can be accomplished through:
  Optimum coagulation/flocculation/sedimentation.
  Degasification / Aeration
  Adsorption with activated carbon
  All of the above

## Slide 103: 20. Which of the following is used to pump a measured dose of liquid chemical into a treatment system?
  Centrifugal Pump
  Actuating Pump
  Positive Displacement Pump
  Gravimetric Feeding Pump

## Slide 104: 21. Chemical feed pumps should be calibrated:
  As per manufacturer recommendations
  When operator notices a problem
  After maintenance
  All of the above

## Slide 105: 22. A good emergency response plan includes:
  Contact Information
  Assessment of Available resources
  Corrective Actions to be taken in emergency situations
  All of the above

## Slide 106: 23. Which form of chlorination will kill Cryptosporidium?
  Chlorine Gas
  Sodium Hypochlorite
  Chlorine Dioxide
  None of the above

## Slide 107: 24. The pump settings for a 30 gpd pump are set at 70% speed and 60% stroke. How many gpd would the pump theoretically feed?
  12.6 gpd
  126 gpd
  12,600 gpd
  126,000 gpd

## Slide 108: 25. Which chemical(s) would increase pH?
  Potassium hydroxide (KOH)
  Calcium Hydroxide (Ca(OH)2)
  Sodium Hydroxide (NaOH)
  All of the above

## Slide 109: 26. The best way to increase dosage of a liquid chemical is to:
  Decrease the stroke
  Increase the stroke
  Decrease the speed
  None of the above

## Slide 110: 27. A check valve that is used to prevent a pump from losing prime:
  Pressure relief valve
  Suction Valve
  Foot Valve
  Anti-Siphon Valve

## Slide 111: 28. Chemicals used at a treatment facility are hazardous to:
  System Employees
  Contractors/Visitors
  Those who live in close proximity to the treatment facility
  All of the above

## Slide 112: 29. A pump calibration determined that a pump was feeding at a rate of 35 mL/min. If the pump typically runs 16 hours, approximately how many gallons of chemical should the operator expect to use? (hint = 3.785 L/gallon)
  About 808 gallons
  About 88 gallons
  About 9 gallons
  About 1 gallon

## Slide 113: 30. A method in which a chemical can be injected at a rate which matches the flow:
  Uniform Injection
  Flow Pacing
  Chemical Monitoring
  None of the above

## Slide 114: 31. An instrument used for accurate determination of the pump’s feed rate:
  Calibration Cylinder
  Strainer Valve
  Injection Assembly
  Foot Valve

## Slide 115: 32. Determine the detention time in minutes of a 100 foot section of 12” main which receives a flow of 35 gpm.
  2,416 minutes
  201 minutes
  107 minutes
  17 minutes

## Slide 116: 33. When evaluating jar test results, evaluate results using:
  A visual evaluation
  Turbidity analysis
  Only B
  Both A and B

## Slide 117: 34. The chlorine dose at a plant is 1.3 mg/L. The system uses 12½% sodium hypochlorite. The flow rate is set at 375,000 gpd. What is the chlorine feed rate in lbs/day?
  32.5 lbs
  325 lbs
  4 lbs
  41 lbs

## Slide 118: 35. Used to produce the vacuum under which vacuum type systems operate:
  Vacuum
  Ejector
  Deductor
  Mixer

## Slide 119: 36. The output of a chemical feed pump is controlled by:
  The length of the plunger stroke
  The number of repetitions of the stroke
  The length of the plunger stroke and the number of repetitions of the stroke
  None of the above

## Slide 120: 37. To help a system combat water hammer – the clanging of pipes caused by a change in direction of flow when a pump shuts off or a valve is closed - a system can install a:
  Backpressure valve
  Pulsation Dampener
  Anti-Siphon Valve
  Negative Pressure Device

## Slide 121: 38. The MSDS states that the specific gravity of alum is 1.32. How much does each gallon of alum weigh?
  6 pounds/gallon
  9 pounds/gallon
  11 pounds/gallon
  15 pounds/gallon

## Slide 122: 39. The capacity of a water to neutralize acids:
  pH
  Alkalinity
  Acid
  Base

## Slide 123: 40. An Emergency Response Plan includes a list of equipment you have on hand in the event of an emergency. This list was developed through:
  An assessment of available resources.
  A supervisor operation module.
  A code of behavior.
  None of the above

## Slide 124: 41. When designing a chemical feed system consider:
  Building redundancy into the system
  Checking the feed pump dosage range
  Both A and B
  None of the above

## Slide 125: 42. The dosage of a coagulant needed to precipitate and remove substances in water solutions is dependent on:
  Amount and types of complexing agents present
  Solution pH
  Sequence in which chemicals are added
  All of the above

## Slide 126: 43. A sedimentation tank holds 20,000 gallons and the flow into the plant is 500 gpm. What is the detention time in minutes?
  10 minutes
  20 minutes
  40 minutes
  80 minutes

## Slide 127: 44. __________ must be activated prior to feeding to obtain expected results.
  Polymer
  Potassium Permanganate
  Chlorine
  Fluoride

## Slide 128: 45. This is used to activate an alarm if unacceptable levels of gas chlorine are sensed in the ambient air of storage and feed rooms.
  Evaporator
  Gas Detector
  Emergency Distributor
  All of the above

## Slide 129: 46. Sequestering agents work by keeping ___________ in solution and prevent the formation of precipitates that could deposit scale or cause discoloration.
  Iron
  Manganese
  Calcium
  All of the above

## Slide 130: 47. The single most valuable tool in operating and controlling a chemical treatment process is the:
  Variable speed, multiple station jar test apparatus
  Treatment series
  Chemical feed systems
  None of the above

## Slide 131: 48. When determining the type of breathing protection needed at a system, consider:
  Level of airborne contamination
  Type of work activity and exposure
  Presence of sufficient oxygen
  All of the above

## Slide 132: 49. The plant flow is set at 2 MGD, an alum dose of 12.0 mg/L is required. How many lbs/day would the plant expect to use?
  50 lbs/day
  100 lbs/day
  200 lbs/day
  400 lbs/day

## Slide 133: 50. When H2SO4 is added to water the pH will:
  Increase
  Decrease
  Neutralize
  Stay the same