State Disinfectant Residual Requirements

| State | Distribution System Residual (mg/L) | Details about Monitoring, Compliance Determinations, etc. | Regulation Citations |
| --- | --- | --- | --- |
| EPA | SW – detectable residual or HPC ≤ 500 | 95% of samples. Detectable is not defined. | 40 CFR § 141.72 (2015) |
| Alabama | 0.2 (free), 0.5 (total) | Daily monitoring. If < 0.2 more than 4 hours, TT violation & PN within 14 days. If < 0.2 more than 24 hours, bacteria samples required. If positive, acute violation & PN. | Ala. Admin. Code r. 335-7-10-.04 (2014) |
| Colorado | 0.2 (free or total) | Measured at TCR sites. Based on # samples - 95%, more than one, one. | 5 Colo. Code Regs. § 1002-11, 11.8(3)(2015) |
| Delaware | 0.3 (free) | Maintain throughout distribution system, daily monitoring at TCR sites, defines detectable as 0.04 | 16 Del. Admin. Code § 4462-8.2 (2015) |
| Florida | 0.2 (free), 0.6 (total) | Maintain at all times. Two or five samples per week based on pop. If < min. residual, increase dose and flush until restored. | Fla. Admin. Code Ann. r. 62-555.350(6) (2015) |
| Georgia | 0.2 (free) | Maintain in all locations. | Ga. Comp. R. & Regs. r. 391-3-5-.14(2) (2013) |
| Illinois | 0.2 (free), 0.5 (total) | Maintain in all locations. Monitor at frequent and regular intervals. | Ill. Adm. Code tit. 35 § 653.604 (2015) |
| Indiana | 0.2 (free), 0.5 (total) | Defines detectable as 0.2 free or 0.5 total. 95% of samples. | 327 Ind. Admin. Code 8-2-1(98) (2015) |
| Iowa | 0.3 (free), 1.5 (total) | Measured at TCR sites. Continuously maintained throughout DS except at dead ends. Defines detectable as 0.1. | Iowa Admin. Code r. 567-42.4(3) (2015) |
| Kansas | 0.2 (free), 1.0 (total) | Daily monitoring. 95% of samples. | Kan. Admin. Regs. § 28-15-19 (2015) |
| Kentucky | 0.2 (free), 0.5 (total) | Daily monitoring. Maintain throughout distribution system. | 401 Ky. Admin. Regs. 8:150 (2015) |
| Louisiana | 0.5 (free or total) | Daily at MRT sites, at TCR sample sites, and at 25% more sites. | La. Admin. Code. Tit 41, § 524, 525 (2015) |
| Minnesota | 0.1 (free or total) | Requires a detectable residual and defines detectable as 0.1. | Minn. R. 4720.3965 (2015) & Minn. R. 4720.0450 (2015) |
| Missouri | 0.2 (total) | Measured at TCR sites. 95% of samples. | Mo. Code. Regs. tit. 10 § 60-4.055(3)&(4) (2015) |
| Nebraska | SW - 0.2 (free), 0.25 or 0.5 (total); GW – 0.1 (free) | 95% of samples. | 179 Neb. Admin. Code 13-005.01D1 (2014) |
| Nevada | 0.05 mg/L (free or total) | Requires a detectable residual and defines detectable as 0.05. | Nev. Admin. Code. § 445A.6683 (2014) |
| New Jersey | 0.05 mg/L (free or total) | Requires a detectable residual and defines detectable as 0.05. | N.J. Admin. Code § 7:10-11.16 & 7:10-1.3 (2015) |
| North Carolina | 0.2 (free), 1.0 (total) | Measured at TCR sites. Must be detectable at MRT sites. | 15 N.C. Admin. Code 18C.2002 (2015) |
| Ohio | 0.2 (free), 1.0 (total) | Measured at TCR sites. 95% of samples. | Ohio Admin. Code 3745-81-72 & 3745-83-01 (2015) |
| Oklahoma | 0.2 (free), 1.0 (total) | Maintain at most distant points. | Okla. Admin. Code § 252:631-3-3 (2014) |
| Pennsylvania | Proposed: 0.20 mg/L (free or total) | Proposed: 95% of samples, monitor daily or weekly, 5% OOC cannot be repeated. | 25 Pa. Code. § 109.710 & 109.301 (2015) |
| Tennessee | 0.2 (free) | Monitor at TCR sites. 95% of samples. | Tenn. Comp. R. & Regs. 0400-45-01-.31 & .17 (2015) |
| Texas | 0.2 (free), 0.5 (total) | Daily or weekly monitoring based on pop. 95% of samples. | 30 Tex. Admin. Code §290.110 (2015) |
| Vermont | 0.1 (free) | Maintain at distant points and defines detectable as 0.1. | 12-030-003 Vt. Code. R. 21 (2015) |
| West Virginia | 0.2 (total) | Minimum at all points. | 64CSR77, 6.4.c |

Source:  Compiled by Pennsylvania DEP, June 2015

Industry Standards:

Great Lakes-Upper Mississippi River Board of State and Provincial Public Health and Environmental Managers, 2012 Edition, Recommended Standards for Waterworks (Ten States Standards):

- Minimum free chlorine residual in a water distribution system should be 0.2 mg/L.

- Minimum chloramine residual, where chloramination is practiced, should be 1.0 mg/L at distant points in the distribution system.

- Higher residuals may be required depending on pH, temperature and other characteristics of the water.

Water Research Foundation, 2010, Criteria for Optimized Distribution Systems:

- Chlorine residual in 95% of measurements:

  - Free chlorine ≥ 0.20 mg/L

  - Total chlorine ≥ 0.50 mg/L