## Slide 1: Module 2O: Corrosion Control & Sequestering
Drinking Water Plant Operator Certification Training
Notes: This module includes material from the DEP 21 hour CCT course.

## Slide 2: Unit 1 – Lead and Copper Rule (LCR)
After this unit, you’ll be able to:
  Describe the major provisions of the LCR
  Describe the sampling protocols for lead and copper tap samples and water quality parameter samples
  Identify selected EPA-approved analytical methods
Notes: Turn to page 1-2 and we’ll review a few terms.

## Slide 3: Examples of Corrosion
Tuberculation
Notes: In addition to the picture on page 1-2, here’s another picture of tuberculation

## Slide 4: Examples of Corrosion
Notes: Here’s a picture of copper corrosion.
Instructor Note: Read highlighted text beginning on page 1-3.

## Slide 5: LCR: Quick Reference Guide
Workbook Pages RG-1 through RG-3:
Consumer Tap Notice – new requirement
Major monitoring provisions
Table 1: Lead & copper tap and water quality parameter (WQP) distribution monitoring
Table 2: Criteria for Reduced lead and copper monitoring
Notes: Beginning on page RG-1, there is a new requirement to the LCR. It’s the consumer tap notice.
  All systems must deliver a consumer tap notice of the lead tap water results within 30 days of learning the results to the persons served by the water at lead and copper tap water sites.
  Systems must submit a copy of the consumer tap notice and a certification form that the notices were distributed by mail or by another method approved by DEP within 3 months of the end of the monitoring period.
  Page RG-2 describes the major monitoring provisions. (Have class turn to page RG-2)
  Table 1 and 2 are found on page RG-3. (Have class turn to page RG-3)

## Slide 6: LCR: Quick Reference Guide
Workbook Pages RG-4 through RG-6:
Treatment Technique and Sampling Requirements if the action level is exceeded
  Water Quality Parameters
  Corrosion Control Treatment
Treatment Technique Requirement if the LEAD action level is exceeded
  Lead Public Education
  Lead Service Line Replacement
Notes:   WQP monitoring is required for small and medium systems if an action level is exceeded. (Have class turn to page RG-4)
Corrosion control treatment is required for small and medium systems if an action level is exceeded.
Large systems must conduct WQP monitoring and corrosion control treatment.
CCT compliance schedule begins at the bottom of page RG-4 and continues on the top of RG-5.
The last table on page RG-5 addresses the requirements when the LEAD action level is exceeded. This table continues on page RG-6.
Lead service line replacement requirements begin at the bottom of RG-6.

## Slide 7: LCR: Quick Reference Guide
Workbook Page RG-7:
Additional LCR Resources links:
  LCR Web page
  Subchapter K of Chapter 109
  EPA LCR documents
Notes:   There are links to additional LCR resources found on page RG-7. (Have class turn to page RG-7)
We are finished with the Quick Reference Guide and now we want to look at a few water sample collection requirements. Turn to page 1-8.

## Slide 8: Key Points
Turn to page 1-11 to summarize the unit key points.
Notes: Instructor Note: After reading each Unit 1 key point, turn to Unit 1 exercise on page 1-12

## Slide 9: Unit 1 Exercise

## Slide 10: Unit 1 Exercise
Sample site | Lead Level (mg/L)
1 | 0.020
2 | 0.018
3 | 0.016
4 | 0.014
5 | 0.011
6 | 0.010
7 | 0.009
8 | 0.008
9 | 0.007
10 | 0.006
2. Based on the following lead tap sample results, what is the 90th percentile value of the following samples? 0.018 mg/L
Is this system exceeding the action level? YES

## Slide 11: Unit 1 Exercise
3. When a small or medium system exceeds an AL, name the first step in the corrosion control treatment activity milestones? Submit a CCT feasibility study within 18 months.

## Slide 12: Unit 1 Exercise
4. Which of the following parameters are considered water quality parameters?
Circle all that apply.
    Temperature
    Conductivity
    pH
    alkalinity
    odor

## Slide 13: Unit 1 Exercise
5. Systems serving 50,000 or less people (i.e. small or medium systems) must collect WQP samples during monitoring periods in which either AL is exceeded.
a. True___X___ b. False______

## Slide 14: Unit 1 Exercise
6. The sample volume size for a lead and copper tap sample is:
500 ml b. 1 liter
An operator must measure pH within 15 minutes of sample collection.

## Slide 15: Unit 1 Exercise
What methodology is NOT an EPA-approved method?
a. Titrimetric
b. Electrometric
c. Colorimetric
d. Color Wheel

## Slide 16: Unit 2 – Corrosion Principles and Theory
After this unit, you’ll be able to:
  Explain chemistry principles that relate to corrosion
  Identify factors which affect corrosion
  Identify the LCR corrosion control treatment alternatives
  Describe important factors affecting each type of treatment
Notes: Turn to page 2-2 and we’ll look at a few chemistry principles.

## Slide 17: Acids
Workbook Page 2-3
Produce H+ ions
Recognized by the “H” in the chemical formula
HCl H+ + Cl-
(Hydrochloric acid)
Notes: Instructor Note: Advance to next slide.

## Slide 18: Bases
Workbook Page 2-4
Produces OH- ions
Recognized by the “OH” at the end of the chemical formula
NaOH Na+ + OH-
(Sodium hydroxide)
Notes: Instructor Note: Advance to next slide.

## Slide 19: Salts
Workbook Page 2-4
No ions are produced (acid and base are neutralized)
Product of combining an acid with a base
HCl + NaOH NaCl + H2O
(Hydrochloric Acid + Sodium hydroxide)
Notes: Now let’s discuss pH on page 2-4.

## Slide 20: The Carbonate System
Workbook Page 2-7
Notes: This visual shows how the carbonate species form at specific pH values.
At pH 4.5, the water contains CARBONIC ACID
As pH increases above 4.5, BICARBONATE begins to form
Above 8.3, CARBONATE begins to form and eventually excess HYDROXIDE ions are formed.
Turn to page 2-8 and we’ll begin our discussion of corrosion principles with a few definitions.

## Slide 21: Corrosion Cell
Workbook Page 2-9
Notes: There are 4 elements necessary for corrosions to occur:
Anode – the part of the metal surface that is corroded because metal dissolves and enters the water as a Pb+2 ion. The 2 “lost” electrons flow to the cathode.
Cathode – where the 2 lost electrons from the anode are “gained” and then leave the metal through the water and return to the anode.
Connection between anode and cathode (pipe) to transport the electrons.
Electrolytic solution (water) to conduct ions between the anode and cathode.
Corrosion will occur as long as this electrical circuit is complete.
Now let’s discuss factors that affect corrosion on page 2-10.

## Slide 22: Eliminating the Corrosion Cell
Workbook Page 2-11
Notes: Corrosion control treatment involves changing the water chemistry to form a thin protective layer on the pipe walls.
When this film covers either the anode or cathode or both, electrons can’t flow and corrosion doesn’t occur.
Changing the water chemistry can make the water less effective in conducting electricity too.

## Slide 23: LCR CCT Alternatives
Workbook Page 2-11
pH/alkalinity adjustment
Calcium hardness adjustment (CaCO3 precipitation)
Corrosion inhibitors
Notes: These are the 3 CCT alternatives under the Lead and Copper Rule that water suppliers may consider.
Turn to page 2-12 and we’ll start with pH/alkalinity adjustment.

## Slide 24: Langelier Saturation Index (LSI)
Workbook Page 2-17
LSI Values | Effect on Water
LSI greater than 0 | Water is supersaturated and tends to precipitate a scale layer of CaCO3
LSI = 0 | Water is saturated (in equilibrium) with CaCO3 so a scale layer of CaCO3 is neither precipitated nor dissolved.
LSI less than 0 | Water is under saturated, tends to dissolve solid CaCO3
Notes: Q. If you had an LSI that is less than 0, is this water scale forming or corrosive? (A: corrosive)
Our 2nd LCR CCT alternative involves calcium carbonate precipitation. This information is found on page 2-17 below the LSI table.

## Slide 25: pH/alkalinity adjustment & Inhibitors
Workbook Page 2-19
Treatment Approach | Key Water Quality Parameters | Appropriate Chemical Feed Systems
pH/alkalinity adjustment | pH, alkalinity, temperature | Caustic Soda Lime Soda Ash Sodium Bicarbonate
Corrosion Inhibitors | pH, alkalinity, temperature, metals, hardness, inhibitor residual | Orthophosphate Polyphosphate Ortho-poly blends Silicates
Notes: The key water quality parameters for pH/alkalinity adjustment are pH, alkalinity and temperature.
The most widely used chemicals for this treatment are caustic soda, lime, soda ash, and sodium bicarbonate.
For corrosion inhibitor treatment, in addition to pH and alkalinity, metals and hardness are important because they may tie up some of the inhibitor and reduce its effectiveness.
The inhibitor concentration itself is a crucial parameter.
The three common phosphate inhibitors are orthophosphates, polyphosphates, and ortho/poly blends.
Silicates are much less common than phosphates, but may be suitable for small systems with iron and manganese problems.
Instructor Note: Advance to next slide.

## Slide 26: Key Points
Turn to page 2-20 to summarize the unit key points.
Notes: Instructor Note: After reading each Unit 2 key point, turn to Unit 2 exercise on page 2-21

## Slide 27: Unit 2 Exercise
1. When placed in water, acids/bases produce hydrogen ions; acids/bases produce hydroxide ions.
2. A salt is the product of combining an acid and a base.

## Slide 28: Unit 2 Exercise
3. A finished water pH value of 5.0 indicates:
  Water is basic
  Water is acidic
  Water may corrode pipes and fittings
  Both a and c
  Both b and c

## Slide 29: Unit 2 Exercise
4. What objectives can be met with corrosion control treatment?
Minimize amount of lead and/or copper dissolving into tap water.
Maximize the service life of plumbing materials.
c. Improve the hydraulic characteristics of water distribution systems.
d. All of the above.

## Slide 30: Unit 2 Exercise
5. Controlling lead/copper is achieved by forming a protective layer on the pipe wall that eliminates the corrosion cell.
True b) False
6. What does a Langelier Saturation Index of 1.1 indicate?
  Scaling potential
  Dissolving potential

## Slide 31: Unit 2 Exercise
7. If an operator adjusts the pH of the finished water above the saturation point for calcium carbonate, this will create a protective coating on the pipe wall.
a) True b) False

## Slide 32: Unit 2 Exercise
If I add: |  | The pH will be ___________ (raised/lowered)
potassium hydroxide | KOH | raised
nitric acid | HNO3 | lowered
lime | Ca(OH)2 | raised
sulfuric acid | H2SO4 | lowered
caustic soda | NaOH | raised
soda ash | Na2CO3 | raised
hydrochloric acid | HCl | lowered
Determine how the addition of the following chemicals to water will affect pH and complete the table.
Notes: Remember any chemical that has an “OH” will raise the pH because it is a base.
Any chemical that has an “H” will lower it because it is an acid.
Soda ash is a salt but also raises the pH.

## Slide 33: Unit 3 – Corrosion Control Chemicals
After this unit, you’ll be able to:
  Identify the common pH/alkalinity adjustment chemicals including:
    common chemical names, characteristics, operational considerations, impacts and constraints
  Identify the common corrosion inhibitors and their impacts and constraints
Notes: Turn to page 3-2.

## Slide 34: pH/Alkalinity Adjustment Chemicals
Chemical Name | Chemical Formula | Common Name
Sodium Hydroxide | NaOH | Caustic Soda
Calcium Hydroxide | Ca(OH)2 | Lime
Sodium Bicarbonate | NaHCO3 | Baking Soda
Sodium Carbonate | Na2CO3 | Soda Ash
Notes: Table 3.1 on page 3-3
You will see these chemicals expressed in one of these 3 ways.
Take a look at the chemical formulas.
Q. Do these chemicals act like acids or bases? (bases) This is a fill-in-the-blank.
Q. Are caustic soda and lime stronger or weaker bases than soda ash or sodium bicarbonate? (stronger) This is a fill-in-the-blank.
Q. Why? (Hydroxides produce a greater pH change for the same dosage than carbonates and bicarbonates.)
Instructor Note: Advance to next slide.

## Slide 35: Table 3.2 Chemical Characteristics
Chemical Name | Use | Notes
Caustic Soda | Raise pH. Convert excess CO2 to alkalinity species | pH control is difficult when applied to low alkalinity water (<20 mg/L)
Lime | Raise pH. Increases alkalinity and calcium content | Slurry feed can cause excess turbidity O & M intensive
Sodium Bicarbonate | Increases alkalinity with little increase in pH | Good alkalinity adjustment choice, but very expensive
Soda Ash | Increases alkalinity with moderate increase in pH | More pH increase caused as compared to sodium bicarbonate, but less costly
Notes: As you can see from Table 3.2 on page 3-4:
Caustic soda, lime, and soda ash raise pH and may increase alkalinity.
Sodium bicarbonate is primarily used to increase alkalinity.
Caustic soda causes the pH to rise dramatically and quickly when alkalinity is low.
Lime requires more operational attention than other chemicals. Look at the Operator Tips for lime on page 3-5:
  Use flexible pipelines to break CaCO3 deposits.
  Minimize length of line by placing feeder as close as possible to point of application.
Instructor Note: Advance to next slide.

## Slide 36: Table 3.3 Operational Considerations
Chemical | Available Forms | Storage | Safety Considerations
Caustic Soda | 50% or 25% solution | 50% solution requires heated storage room to prevent freezing | dangerous to handle, use protective clothing, rubber gloves, rubber apron, face shield, goggles control mists with good ventilation
Lime | powder in 50 or 100 lb bags; bulk | Dry storage with slurry feed | positive ventilation, protective clothing, gloves, face shield, neck cloth, respirator
Sodium Bicarbonate | powder; 25 lb drums, 100 lb bags | Dry storage with solution feed | positive ventilation, protective clothing, gloves, goggles, respirator
Soda Ash | powder in 50 and 100 lb bags; bulk | Dry storage with solution feed | positive ventilation, protective clothing, gloves, goggles, respirator
Notes: Lime, sodium bicarbonate, and soda ash are delivered as dry chemicals but are fed as liquids.
Soda ash and sodium bicarbonate are safe and easy chemicals to handle.
Caustic soda is typically sold as a 25% or 50% solution.
Caustic soda is dangerous to handle.
  Causes severe burns to skin and eyes and mucous membranes
  Causes severe lung damage if dust, mist or spray is inhaled
  Reacts violently with water, acids, and other substances
Recently, 20 people sought medical attention for skin, eye, and throat irritations after caustic soda was accidentally released into a water system in a southwest Florida community. About 8,000 gallons of water containing high levels of caustic soda was supposed to be flushed away, but instead was released into the city’s water supply.
If this happened as a result of ingesting water, just imagine how much harm you could do to yourself by handling it improperly.
If you are using caustic soda, pay special attention to the MSDS sheet, which is located in the Appendix.
Instructor Note: Advance to next slide.

## Slide 37: Personnel Safety Protection
Workbook Page 3-6, 3-7
Protective clothing
Showers/eye wash equipment
First Aid
Notes: Protective clothing includes:
    Eye protection. (goggles, full-face shield)
    Chemical-Resistant Gloves.
    Impervious protective clothing and/or rubber apron.
  Emergency showers and eye-wash stations should be provided.
  To address the first aid measures, turn to page 3-8:
  For Skin or Eye Contact:
Immediately shower with large quantities of water.
Remove protective clothing and equipment while in the shower.
Flush the skin or eye with water for at least 15 minutes.
  For ingestion:
    Don’t induce vomiting, give 2 glasses of water to dilute.
  Turn to page 3-9 and look at the caustic soda operator tips.

## Slide 38: Key Points
Turn to page 3-18 to summarize the unit key points.
Notes: Instructor Note: After reading each Unit 3 key point, turn to Unit 3 exercise on page 3-19

## Slide 39: Unit 3 Exercise
List the common names for the following pH/alkalinity adjustment chemicals:
Chemical Name Common Name
Calcium hydroxide Lime
Sodium carbonate Soda Ash
Sodium hydroxide Caustic soda

## Slide 40: Unit 3 Exercise
When using caustic soda, it is necessary to have at least 20 mg/L of alkalinity to maintain a stable pH.
a) True b) False
It is not necessary to minimize the length of line for a lime feeder.
a) True b) False

## Slide 41: Unit 3 Exercise
Which type of inhibitor is used to control lead?
Polyphosphate
Silicates
Orthophosphate
When the pH is raised before disinfection, the inactivation effectiveness of free chlorine is increased.
a) True b) False

## Slide 42: Unit 3 Exercise
6. When using polyphosphates to sequester iron and manganese, why should the chemical feed point should be located before the disinfection process?
To avoid oxidizing the iron and manganese with the chlorine which would create iron and manganese precipitates to be pumped out into the distribution system.

## Slide 43: Unit 4 – Chemical Feed
After this unit, you’ll be able to:
  Identify components of liquid and dry feed systems
  Describe liquid and dry feed operation and maintenance activities
  Perform calculations for the following types of situations:
    Mixing a % solution
    Determining Weight of % solution using specific gravity
    Dry and liquid feed calculations
    Calculating the “Active Ingredient” Weight of a % solution
Notes: Instructor Note: Advance to next slide for final objective.

## Slide 44: Unit 4 – Chemical Feed Objectives
After this unit, you’ll be able to:
  Describe the steps in developing a pump calibration curve
Notes: Instructor Note: Advance to next slide.

## Slide 45
Components of a Liquid Chemical Feed System
Notes: Let’s start with the first component which is the chemical storage container.
Chemical storage containers could be:
  Chemical drum to feed a neat solution (undiluted)
  Day tank to store, dilute or mix chemicals.
Tanks should have:
A measuring device to measure amount of chemical in tank.
Spill containment large enough to contain a spill of 110% of the largest spill container.
Leak detection alarm in the event of a chemical spill.
Suction assembly located above the bottom of the storage tank to avoid pulling in solids.
  Suction strainer
  Foot valve to prevent the pump from losing prime.
Calibration Cylinder that consists of a graduated cylinder located on the suction side of the pump to determine pump’s feed rate.

## Slide 46
6
. Injector Assembly
5
.
Pulsation Damper
4
. Four
–
Function Valve
*Anti
-
Siphon
*Backpressure Relief
*Pressure Relief
*Priming Function
7
.
Metering
Pump
Flow
Components of a Liquid Chemical Feed System
Notes: Here’s the upper half of the Figure 4.1 diagram on page 4-2 .
4-Function Value that provides:
  Anti-siphon valve prevents siphoning of the chemical storage tank into the distribution system when negative pressure is produced.
  Backpressure valve maintains a steady backpressure and prevents over pumping when little or no backpressure is present.
  Pressure relief value dissipates excess pressure.
  Priming function to prime the pump.
Pulsation Dampener offsets surges created by the pulsating discharge pressure of a piston or diaphragm metering pump. It helps combat water hammer.
Injector Assembly discharge point should be located in the middle of the flow to assure proper mixing.
Metering pump to pump a measured dose of liquid chemical into the treatment system. Turn to page 4-4 and we’ll continue discussing liquid chemical feed components.

## Slide 47: Weight of Gallon of Solution
Example: 50% caustic soda (NaOH) has a specific gravity of 1.53
Wt of Substance = (Specific gravity of solution x 8.34)
Wt of NaOH, lbs/gal = 1.53 X 8.34
Wt of NaOH = 12.76 lbs
Each gallon of NaOH weighs 12.76 lbs
Notes: We’ll use weight and specific gravity when we calculate liquid feed dosage rates later in this unit.
Turn to page 4-13 and we’ll begin our discussion of chemical feed rate calculations.

## Slide 48: Davidson Pie
Notes: This diagram can be used to solve for 3 different results: dosage, feed rate, and flow (or volume).
As long as you have 2 of those 3 variables, you can solve for the missing variable.
Davidson Pie Interpretation
Middle line = divided by (÷) Bottom diagonal lines = multiply by (x)
In other words, here are the 3 equations that can be used with these variables:
1. Feed Rate, lbs/day = Flow (MGD) or Volume (MG) x Dosage (mg/L) x 8.34 (which is the density of water)
2. Flow (MGD) = lb/day ÷ (Dosage, mg/L x 8.34)
3. Dosage (mg/L) = lb/day ÷ (Flow, MGD x 8.34)
We’ll only need to focus on the first and most commonly used equation that solves for feed rate in lbs/day.

## Slide 49: Davidson Pie
lbs
Day
8.34
mg
L
MGD
Feed Rate
Flow
Dosage
Notes: Dry Feed Rate Calculation
Feed Rate, lbs/day (covered by blue shading) = Flow(MGD) x Dose(mg/L) x (8.34)
Turn to page 4-16 and we’ll use this equation to solve a dry feed rate calculation.

## Slide 50: “Active Ingredient” Weight
Within this 25% NaOH solution, the active ingredients are yellow. Calculate the “yellow” weight by:
Solving weight equation for a gallon of solution using specific gravity
  Wt, lbs/gal = (Specific gravity x 8.34)
1.28 X 8.34 = 10.67 lbs/gal
Determining “active ingredient” wt based on % purity
  Convert % purity of solution into a decimal
25% = 0.25
  Multiply weight of a gallon of solution by % purity
10.67 lbs/gal (Step 1 weight) X 0.25 (% purity) = 2.66 lbs/gal of
yellow “active ingredients”
Within the 10.67 lbs of 25% solution, there are 2.66 lbs of “active ingredients”.
Notes: This explanation is found on page 4-20.
Let’s practice calculating the active ingredient weight on page 4-21.

## Slide 51: Converting from lbs/day to gal/day
Steps 1 & 2: Calculates the “active ingredient” weight
Step 3: Converts flow into MGD
Step 4: Solves lbs/day feed rate equation for 100% pure chemical
Step 5: Uses unit cancellation to convert lbs/day to gal/day
Notes: To summarize the steps on page 4-22 that we use to do to convert the feed rate of lbs/day into gal/day.
Steps 1 & 2 calculate the “active ingredient” weight. (We practiced steps 1 & 2 in our last activity).
Steps 3 & 4 relate to solving the feed rate equation for “lbs/day”
Step 5 combines the “active ingredient” weight in step 1 with the feed rate in step 4.
  Notice we invert 2.66 lbs/gal data set to position the numerator unit “gallon”
Turn to page 4-23 to practice this type of conversion.

## Slide 52: Pump Calibration Table
60% Stroke Pump Calibration Table |  |  |  | 
Pump Speed Setting | Volume Pumped (mL) | Time (sec) | Feed Rate (mL/min) | Feed Rate (gal/day)
20 | 65.6 | 55 | 71.56 | 27.2
40 | 141.9 | 59 | 144.31 | 54.8
60 | 249.1 | 61 | 245.02 | 93.1
80 | 195.2 | 32 | 366.0 | 139.1
100 | 267.4 | 35 | 458.40 | 174.2
Notes: Figure 4.4 on page 4-25
Here’s a completed liquid feed pump calibration table for the 60% Stroke setting. An operator would create a table like this for each stroke setting from 20% to 100%.
Instructor Note: If someone asks about how to convert mL/min into gal/day in the last column in 4.4:
?gal = 1 gal X 71.56 mL X 1440 mins= 27.22 gal
day 3785 mL min day day
Since we solved the feed rate problems for “gal/day”, this is how we convert what we measured in “mL/min” during the pump calibration to the proper dosage in “gal/day”.

## Slide 53: Pump Calibration Curve for 60% Stroke
Notes: After determining the actual feed pump output for each stroke setting and recording it on the pump calibration table, an operator would create a pump calibration curve for each % stroke table.
Figure 4.5
Here’s the pump calibration curve for the 60% stroke data we just reviewed.
Turn to page 4-28 and we’ll review a few operator tips about pump calibration.

## Slide 54: Pump Calibration Curve for 60% Stroke
Notes: The final step in the pump calibration activity
Step 3 – Select the pump setting from all the % stroke calibration tables that provides the calculated feed rate.
The optimal pump setting would take into account:
The dosage required.
The manufacturer’s recommendations for minimum and maximum settings.
The linearity of the “curves”. A more linear (straight) curve is better.
Once the appropriate percent stroke setting has been determined, future calibration would only involve the speed range (20-100) at that percent stroke.
Instructor Note: Advance to next slide.

## Slide 55: Key Points
Turn to page 4-30 to summarize the unit key points.
Notes: Instructor Note: After reading each Unit 4 key point, turn to Unit 4 exercise on page 4-32

## Slide 56: Unit 4 Exercise
Liquid chemical feed components consist of:
  Chemical Storage
  Calibration cylinder
  Metering Pump
  Pulsation Damper
  All of the above

## Slide 57: Unit 4 Exercise
Secondary spill containment areas should be provided and include leak detection equipment to provide an alarm in the event of a chemical spill or leak.
a) True b) False

## Slide 58: Unit 4 Exercise
The foot valve is used to prevent the pump from losing prime.
A clogged suction assembly can be cleaned with a weak acid solution (i.e., vinegar or 1:1HCL).
a) True b) False

## Slide 59: Unit 4 Exercise
Volumetric/Gravimetric dry feeders are extremely accurate.

## Slide 60: Unit 4 Exercise
6. Chemical feed calculations involve 4 considerations:
Dosage
Plant Flow
Chemical Product Strength
Product Feed Rate
7. Chlorine dose = chlorine demand (mg/L) + chlorine residual (mg/L).

## Slide 61: Unit 4 Exercise
Why should the discharge point of the injector assembly should be located in the middle of the flow of the pipe?
  To provide proper mixing.
8. A pump calibration curve plots feed rate delivery versus the pump setting.